REX— C100 SERIES INSTRUCTION MANUAL

IMNZC17-E3

Before operating this Instrument, please carefully read this manual and fully understand its contents. And always keep it around you to make it available easily anytime.

WARNING

.If failure or error of this instrument could result in a critical accident of the system, install an external protection circuit to prevent such an accident.

.Do not turn on the power supply until all of the wiring is completed. Otherwise electric shock, fire or malfunction may result.

.Use this instrument within the scope of its specifications. Otherwise fire or malfunction may result.

.Do not use this instrument in the places subject to flammable or explosive gas.

.Do not touch high-voltage blocks such as power supply terminals, etc. Otherwise electric shock may result.

.Never disassembles, repair or modify the instrument. This may cause electric shock, fire or malfunction.

CAUTION

•	This is a Class A instrument, the domestic environment this instrument may cause radio interference, in which case the user is required to take adequate measures.

•	This instrument is protected from electric shock by reinforced insulation. So please arrange reinforced insulation to the wire for input signal against the wires for instrument power supply, source of power and roads as far as possible.

•	This instrument is manufactured on the assumption that It Is used in the condition of being mounted on the instrumentation panel. Therefore, take the necessary measures on the equipment side mounted with this instrument so that the operator or other personnel are not accessible to high-voltage blocks In this instrument such as power supply terminals, etc.

•	Always observe precautions described in this manual. Otherwise serious injury or accident may result

•	Conduct ail of the wiring in accordance with the local codes and regulations.

•	Install a protection device such as a fuse, etc. In the power supply, input or output line, if necessary.

•	Do not allow metal fragments or lead wire scraps to fall inside this instrument. This may cause electric shock, fire or malfunction.

•	Firmly tighten each terminal screw at the specified torque. Otherwise electric shock or fire may result.

•	Do not place any obstacle around this instrument in order not to impede radiation of heat. And do not close ventilation holes.

•	Do not connect wires to unused terminals.

•	Before cleaning the instrument, always turn off the power supply.

•	Remove stains from this instrument using a soft, dry cloth. Do not use a volatile solvent such as thinner in order to avoid deformation or discoloration.

•	Do not rub nor strike the display unit of this instrument with a hard object.

Notice

•This manual is subject to change without prior notice.

•Examples of figures, diagrams and numeric values used in this manual are for a better understanding of the text, but not for assuring the resultant operation.

•This manual may not be reproduced or copied in whole or in part without RKC's prior consent.

•RKC assumes no responsibility for any of the following damage which the user or third party may suffer.

•Damage incurred as a result of using this product

•Damage caused by product failure which cannot be predicted by RKC

•Other indirect damage

•in order to use this instrument continuously and safety, periodic maintenance is required. Some of components and parts used in this instrument have a limited service life, or deteriorate overtime.

1. PRODUCT CHECK

Check whether the delivered product is as specified by referring to the following model code list.

■Model code

C 1 0 0

(1) Control action                      (5) First alarm [ALM1]	     (6) Second alarm [ALM2]

F:  PID action [Reverse action]	  N: No first alarm	                      N: No second alarm

D: PID action [Direct action]	  A: Deviation high alarm *2	A : Deviation high alarm *2

B: Deviation low alarm *2	 B: Deviation low alarm *2

(2)	Input type                       C: Deviation high/low alarm*2    C: Deviation high/low alarm*2

See input range table “Code"     D: Band alarm	                      D: Band alarm

E: Deviation high alarm *3        E: Deviation high alarm *3

(3)  Input range                            F: Deviation low alarm *3	 F: Deviation low alarm *3

See input range table "Code”	G: Deviation high/low alarm*3 	G: Deviation high/low alarm*3

H: Process high alarm *2	    H: Process high alarm *2

(4) Control output [OUT]            J: Process low alarm *2	               J: Process low alarm *2

M: Relay contact	                        K: Process high alarm *3  	    K: Process  high alarm*3

V: Voltage pulse	                        L: Process low alarm *3   	    L: Process low alarm *3

B: Current 4 to 20mA DC             R : Control loop break alarm *4   P: Heater break alarm (CTL-6)

G: Trigger (for triac driving) *1	                                                           S: Heater break alarm (CTL-12)

R : Control loop break alarm *4

*1 When control output is trigger output for triac  driving, only the first alarm is available.

• Confirm that power supply voltage is also the same as	that specified when ordering.

*2 Without hold action.

*3 With  hold action.

*4 As control loop break alarm, only either the first alarm or second alarm is sele

Accessories

•Mounting brackets... 2 pcs.                • Instruction manual (IMNZC17-E3)... 1 copy

2 MOUNTING

WARNING

•in order to prevent electric shock or instrument failure, do not turn on the power supply until all of the wiring is completed.

■Cautions for mounting

Avoid the following when selecting the mounting location.

•Ambient temperature of less than 0 C (122 *F) or more than 50 C (32 *F).

•Ambient humidity of less than 45% or more than 85% RH .

•Rapid changes in ambient temperature which may cause condensation.

•Corrosive or inflammable gases.

•Direct vibration or shock to the mainframe.

•Water, oil, chemicals, vapor or steam splashes. •Excessive dust, salt or iron particles.

•Excessive induction noise, static electricity, magnetic fields or noise.

•Direct air flow from an air conditioner.

•Should be used indoors where the system is not exposed to direct sunlight.

Heat to be accumulated radiation heat.

4  НАЗВАНИЯ ЧАСТЕЙ

(1)Set (SET) ke

(2)Setting digit shift key

(3)  Set-value decrement key

(4)  Set-value increment key

(5)  Measured-value (PV) display unit (Green)

(6)  Set-value(SV) display unit (Orange)

(7)  Control output (OUT) lamp (Green)

(8)  Auto-tuning (AT) lamp (Green)

(9)  First alarm (ALM1) lamp (Red)

(10) Second alarm (ALM2) lamp (Red)

5. OPERATION

■Calling—up procedure of each mode

: Press the (SET)key.

: Press the (SET) key for more than 5 sec.

(Power-ON)

Input type code display         Тип входа отображения кода

Input range display                Дисплей Входной диапазон

- ->

When no key is operated for more than 1 minute.

Если ни одна кнопка не работает в течение более 1 минуты

PV/SV режим отображения             display mode

<-

(Displayed for about 4 sec.)  (Отображается в течение 4 сек)

Display changes automatically.  Показать изменения автоматически.

SV режим настройки                  setting mode

Параметр режимa настройки

Alarm setting   уставка сигнализации

Input type code/input range display

Other  setting

Auto-tuning

This controller, with the power turned ON, displays automatically the input type code on the measured-value (PV) display unit and the input range, on the set-value (SV) display unit, respectively.

Example:

For a controller with the К thermocouple input type and input range from 0 to 1372 °C

(1)Displays the input type code

: Indicates input abbreviation.

: Indicates engineering unit.

(°F : F)

: Indicates input type.

(2)Displays the input range

■Parameter type

The following parameter symbols are displayed one by one every time the (SET) key is pressed. However, some parameter symbols may not be displayed depending on the specification.

•The second alarm (or first alarm), heater break alarm, control loop break alarm parameter symbols are not simultaneously displayed.

•Heater break alarm is not available on a current output.

■   Parameter setting procedure

• Setting set-value (SV)

Following is an example of setting the set-value (SV) to 200 *С.

(1) Press the (SET) key to enter the SV setting mode.

The digit which light brightly is settable.

(2) Press the  key to shift the digit which lights brightly up to the hundreds digit.

(3)Press the   key to "2". Pressing the  key increments numerals, and pressing the  key decrements numerals.

(4) After finishing the setting, press the (SET) key.

All of the set-value digits light brightly and as a result the controller returns to the PV/SV

display mode.